Subject:

Intumescent paint for FRFC column 4B fire test

Description:

Primary layer : - Thickness to apply : one 40 μm layer of 7E-450 C-THERM PRIMER - Quantity to apply : - Surface to paint : 2,52 m² - PRIMER paint allows 11,17 m²/l at 40 μm/layer - PRIMER specific gravity : 1,47 g/ml  226 ml/40 μm layer or 332 g/40 μm layer - Planning : 15/12/08 (midday) Secondary layers : - Thickness to apply : - Section factor = 205 m-1 - Fire resistance foreseen : 60 min Rf  Thickness to apply : 1968 μm layer of 7H-960 C-THERM HB - Thickness applied with a brush : 400 μm/layer  five layers of 7H-960 C-THERM HB - Quantity to apply : - Surface to paint : 2,52 m² - HB paint allows 1,72 m²/l at 400 μm/layer - HB specific gravity : 1,32 g/ml  5x1442 ml/(1968/5) μm layer or 5x1903 g/(1968/5) μm layer - Planning : - Layer 1 : 16/12/08 (morning) - Layer 2 : 16/12/08 (afternoon) - Layer 3 : 18/12/08 (afternoon) - Layer 4 : 19/12/08 (morning) - Layer 5 : not applied  4 layers have been painted (and not 5)