## Slide 1: Hosting capacity of low-voltage distribution networks
Amina Benzerga
Doctoral thesis public defence
December 6th , 2024

## Slide 2
(Image from https://www.synox.io/cat-smart-energy/smart-grid-definition)

## Slide 3: Power System
Traditional power system, one way power flow.
Demand
Production

## Slide 4: Power System
Demand
Production

## Slide 5: Power System
Production
Demand / Production

## Slide 6: Distributed Energy Resources (DERs)
Small-scale energy assets that generate, store or consume energy.
e.g.:

## Slide 7
NEWS
BREAKING

## Slide 8: DERs issues – Photovoltaic (PV) panels example

## Slide 9: DERs issues – Electrical Vehicle (EV) example

## Slide 10: DERs issues
Two examples of issues from the network point of view:
  Voltage rises or drops (produce or consume more than expected, beyond voltage limits)
  Congestion (due to high demand, network limits to deliver electricity are reached)

## Slide 11: The scope of this thesis
The hosting capacity is the amount of new resources that can be hosted by a network before facing any issues, i.e., compromising its operational limits or violating safety constraints.
Amount of photovoltaic panels
Performance indicator
Hosting capacity
Unacceptable operation
Acceptable operation

## Slide 12
Topology identification
Single technology HC
Unified HC definition
Combined HC

## Slide 13: Topology identification

## Slide 15
Street map

## Slide 16
Electrical network topology
Substation
Feeder 1
Feeder 2
Feeder 3
Feeder 4

## Slide 17
Electrical network topology
Substation
Feeder 1
Feeder 2
Feeder 3
Feeder 4
Phase 1
Phase 2
Phase 3

## Slide 18
Smart meters
Substation
Feeder 1
Feeder 2
Feeder 3
Feeder 4
Phase 1
Phase 2
Phase 3
Smart-meters

## Slide 19
Available data

## Slide 20
Topology reconstruction goal

## Slide 21: Assumptions
During the observation period, the network topology does not change
Customer connections to the main feeder are single-phase
Customers connection phase is known
There is at least one smart-meter connected at every phase of every feeder
Three-phase measurements of feeders at the substation are available

## Slide 22: Methodology
Two steps:
  1. Construct single-phase estimates of the network topology for each.
  2. Merge the three single-phase estimated typologies to form a three-phase feeder model
Metered nodes
Single-phase topologies
Three-phase topology
Step 1
Step 2

## Slide 23: Methodology – single phase reconstruction
Available data
Real network
Topology estimation
Topology validation
Unavailable

## Slide 24: Methodology – single phase reconstruction
Hidden nodes detection

## Slide 25: Methodology – single phase reconstruction
Real network
Available data
Topology estimation
Topology validation
Unavailable
Hidden node detection
Single phase reconstruction

## Slide 26: Methodology
Two steps:
  1. Construct single-phase estimates of the network topology for each.
  2. Merge the three single-phase estimated typologies to form a three-phase feeder model
Metered nodes
Single-phase topologies
Three-phase topology
Step 1
Step 2

## Slide 27: Methodology – Three-phase topology formation
Feeder 1

## Slide 28: Methodology – three-phase topology formation
Feeder 1
Feeder 2
Feeder 3

## Slide 29: Methodology – three-phase topology formation
Feeder 1

## Slide 30: Methodology – three-phase topology formation
Feeder 3
Feeder 2
Three-phase topology

## Slide 31: Methodology
Two steps:
  1. Construct single-phase estimates of the network topology for each.
  2. Merge the three single-phase estimated typologies to form a three-phase feeder model
Metered nodes
Single-phase topologies
Three-phase topology
Step 1
Step 2

## Slide 32: Test case
1 substation (red dot)
4 feeders
216 nodes
128 customers
52 Smart meters (black rectangles)

## Slide 33: Results

## Slide 34: Results

## Slide 35: Results validation

## Slide 36
Topology identification
Single technology HC
Unified HC definition
Combined HC

## Slide 37: Determining a Hosting Capacity

## Slide 38: Single technology hosting capacity
For a given technology, how many of that technology can we install before facing any issues?

## Slide 39
Add new technologies (e.g. PV, EV) to a network and simulate over time and see what happens !
Methodology idea

## Slide 40: Key performance indicators
Measure of the performance of the network.
Amount of photovoltaic panels
Performance indicator
Hosting capacity
Unacceptable operation
Acceptable operation

## Slide 41: Configurations
12 Photovoltaic panels
No issues
Issues

## Slide 42: Configurations
12 Photovoltaic panels

## Slide 43: Configurations (2)
For instance, for 40 new installations and 100 customers, there are possible configurations.
Probability density function (PDF) for the indicators:
Performance indicator
Density

## Slide 44: Methodology - summary
Initial network
Select type:
For each penetration rate (e.g. amount of PV):
Number of configurations
…
Power flow
Power flow
Performance indicators
Performance indicators
Performance indicator
Density

## Slide 45: Test case
Topology reconstructed
500 configurations per penetration
1 week time series
Penetrations [0, 1, …, 100]
13 PVs of 290 W
peak

## Slide 46: PV Performance indicator – Energy spilled

## Slide 47: PV Performance indicator – Energy spilled

## Slide 48: PV Performance indicator – Energy spilled
Energy spilled

## Slide 49: Test case – PV results

## Slide 50: Test case – PV results
Q1
Q3

## Slide 51: Test case – PV results

## Slide 52: Test case – PV results

## Slide 53
Topology identification
Single technology HC
Unified HC definition
Combined HC

## Slide 54: Hosting Capacity Definition

## Slide 55: Hosting capacity (HC)
The HC is the amount of new resources (DER) that can be hosted by a network before facing any issues, i.e., compromising its operational limits or violating safety constraints.
Performance indicator
Hosting capacity
Unacceptable operation
Acceptable operation
Amount of DER

## Slide 56
For a given network, with customers

## Slide 57
These customers can add different types of DERs with different options, for instance their size.
State:

## Slide 58
Scenario:

## Slide 59
Scenario ….:
Set of scenarios :
Scenario 1:
Scenario 2:
Scenario 3:
Set of considered scenarios :

## Slide 60
Penetration :
A scenario :

## Slide 61
Set of penetrations
Scenario 1:
Scenario 2:
Scenario 3:
Scenario ….:
Set of scenarios :
Set of considered scenarios :
…
Set of considered penetrations
…

## Slide 62
Exogenous data

## Slide 63
Scenarios
Penetrations
Notes: -

## Slide 64
Scenarios
Penetrations
Considered Scenarios

## Slide 65
Scenarios
Penetrations
Considered scenarios
Considered penetrations

## Slide 66
Scenarios
Penetrations
Considered scenarios
Considered penetrations
Valid scenarios

## Slide 67
Scenarios
Penetrations
Valid scenarios
Considered scenarios
Considered penetrations
Valid penetrations

## Slide 68
Scenarios
Penetrations
Considered scenarios
Valid scenarios
Considered penetrations
Valid penetrations
Invalid scenarios

## Slide 69
Invalid scenarios
Considered scenarios
Valid scenarios
Considered penetrations
Valid penetrations
Invalid penetrations
Scenarios
Penetrations

## Slide 70
Invalid scenarios
Considered scenarios
Valid scenarios
Considered penetrations
Valid penetrations
Invalid penetrations
Scenarios
Penetrations
Feasible penetrations

## Slide 71
Invalid scenarios
Considered scenarios
Valid scenarios
Scenarios
Penetrations
Considered penetrations
Valid penetrations
Invalid penetrations
Feasible penetrations
Feasible scenarios

## Slide 72: N-dimensional hosting capacity

## Slide 73: One Dimensional Hosting capacity
Number of Photovoltaic panels
Feasible penetrations
Safe penetrations

## Slide 74: Summary of the formalism
Valid / invalid sets
Exogenous data
A network
Technologies
Options for the technologies
t=…
Penetrations
State
Feasible/safe penetrations
Hosting capacity
Scenario

## Slide 75
Topology identification
Single technology HC
Unified HC definition
Combined HC

## Slide 76: Combined PV-EV-HP Hosting Capacity

## Slide 77: Methodology
Considered scenarios
Penetrations
Issues

## Slide 78: Case study – considered scenarios
Technologies size:
Photovoltaic size: 20 x 290W
Electric vehicle charger sizes: 3kW and 7kW
Heat pump sizes: 7.5kW and 15kW
peak
Probability of installing a technology:
Use a probability to install a new technology for each customer and technology type.

## Slide 79: Case study
Representative days:
  Reduce the number of time steps considered

## Slide 80: Case study – Functions
Issues:
Penetrations:
Number of customers with new technologies (DERs)
Total number of customers
Under-voltage limit
Over-voltage limit
Node voltage
Loads of a line
Line capacity
<
<
<

## Slide 81: Case study – Belgian network
1 substation
2 feeders
23 customers
15 customers with Smart Meters
Penetration levels:
  [25%, 50%, 75%, 100%]
100 scenarios per penetration level

## Slide 82: Results - Voltage

## Slide 83: Results - Voltage
25% PV
25% EV

## Slide 84: Results - Voltage
Acceptable for a penetration around 50% for all technologies
Under-voltage is encountered rapidly for both EV and HP penetrations higher than 50%.
Over-voltage is not faced before 75% of PV penetration.

## Slide 85: Results – Loads
Even with high penetration rates for all three technologies, the lines of the case study network are not overloaded.

## Slide 86
Topology identification
Single technology HC
Unified HC definition
Combined HC

## Slide 87: Conclusion – Journey summary
In this presentation:
Reconstruction of the topology of distribution network using smart meter data
Single technology hosting capacity methodology with application on a Belgian inspired network with photovoltaic panels.
Definition of the hosting capacity
Combined hosting capacity of PV-EV-HP
In addition, in the manuscript:
Impact of optimal phase connection on HC

## Slide 88: Future work
Representative days
Socio-economic behaviour
Coupling the HC formalism with investment strategies and active network management.

## Slide 89: Further information
In the thesis:
  A. Benzerga, “Hosting Capacity of Low-Voltage Distribution Networks”, https://hdl.handle.net/2268/323245
And the corresponding papers:
  Benzerga, A., Maruli, D., Sutera, A., Bahmanyar, A., Mathieu, S., & Ernst, D. (2021, June). Low-voltage network topology and impedance identification using smart meter measurements. In 2021 IEEE Madrid PowerTech (pp. 1-6). IEEE.
  Marulli, D., Mathieu, S., Benzerga, A., Sutera, A., & Ernst, D. (2021, October). Reconstruction of low-voltage networks with limited observability. In 2021 IEEE PES Innovative Smart Grid Technologies Europe (ISGT Europe) (pp. 1-5). IEEE.
  Benzerga, A., Mathieu, S., Bahmanyar, A., & Ernst, D. (2021, July). Probabilistic capacity assessment for three-phase low-voltage distribution networks. In 2021 IEEE 15th International Conference on Compatibility, Power Electronics and Power Engineering (CPE-POWERENG) (pp. 1-6). IEEE.

## Slide 90: And more
  Benzerga, A., Bahmanyar, A., Derval, G., & Ernst, D. (2024). A unified definition of hosting capacity, applications and review. ORBi-University of Liège. https://orbi.uliege.be/handle/2268/315915.
  Benzerga A., Vassallo M., Gerard S., Vandeburie J., and Ernst D. (2024). Combined PV-EV-HP Hosting Capacity Analysis of a Belgian Low- Voltage Distribution Network. In Proceeding of the 34th Australasian Universities Power Engineering Conference (AUPEC). 2024.
  Benzerga, A., Bahmanyar, A., & Ernst, D. (2022). Optimal Connection Phase Selection of Residential Distributed Energy Resources and its Impact on Aggregated Demand. arXiv preprint arXiv:2207.05059.
  Benzerga, A., Gérard, S., Lachi, S., Garnier, Q., Bahmanyar, A., & Ernst, D. (2022). Optimal connection phase selection for single-phase electrical vehicle chargers.
  Vassallo, M., Benzerga, A., Bahmanyar, A., & Ernst, D. (2023, June). Fair reinforcement learning algorithm for pv active control in lv distribution networks. In 2023 International Conference on Clean Electrical Power (ICCEP) (pp. 796-802). IEEE.

## Slide 91
“Happiness can be found, even in the darkest of times, if one only remembers to turn on the light.”
- Albus Dumbledore